## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
Heat Recovery Project: Heat of Compression Desiccant Dryers
Hank van Ormer, Air Power USA
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 6
Introduction
Compressed Air Best Practices® Magazine
Heat Recovery Project: Heat of Compression Desiccant Dryers

## Slide 7: About the Speaker
Founded Air Power USA in 1986
Over 50 years of experience in the compressed air and gas industry
Hank van Ormer
Air Power USA
Sponsored by

## Slide 8
Heat of Compression Energy Recovery Operation – Basic Technology of HOC Desiccant Air Dryers & Other Heat Recovery Projects
May 16, 2019
Air Power USA
Hank van Ormer – Technical Director
(740) 862-4112
1

## Slide 9: Introduction: Heat of Compression
What is Heat of Compression? Is it a phenomena? What is the technical support for HOC “existence”?
  HOC is generated during the compression phase in any gas or air compressor.
  The magnitude is driven by the basic inefficiency of the work delivered by the compressed air and gas to the process.
  HOC is expressed or measured in BTU’s per hour.
HOC reflects the basic inefficiency of compressed air or gas as a transfer of power/energy.
Example: 100 psig of compressed air requires 8hp to the compressor to produce 1hp of “work” at the process. The 7hp worth of work that went in to the compressed the air or gas was not delivered to the work process and the energy stays in the system as HEAT. This energy can be perceived as a problem to be cooled or a source of energy to be recovered.
2

## Slide 10: Where Does HOC Come From?
The technical support for “Heat of compression” comes from “energy can neither be created nor destroyed”. Remember high school physics class?
8hp of power in = 1hp of electric power delivered to the process for work
(1hp = 2,546 BTU/hr. / 7hp = 17,852 BTU/hr. HOC stored and not delivered to the process)
Example: 2,546 BTU/hr. -- 17,852 BTU/hr. = stored HOC energy which is still available to recover and use the energy in other projects.
This “heat” is often referred to as “free” since all the cost to produce it is the compression of the gas/air which is covered by the cost of operating the compressor.
Recovered heat will offer the plant another heat source and the opportunity will reduce plant operating energy costs.
10
3

## Slide 11: Recoverable Heat of Compression
All air compressors generate heat of compression. What they generate can be recovered and utilized.
HOC offers a potential energy recovery of up to 85-90% of the total motor hp in the form of heated cooling air, water or oil.
  Cooling water probable discharge temperature of up to 130°F
  Cooling air probable discharge temp 5°F to 20°F above ambient
  Coolant from injected lubricant cooling, rotary screw, scroll etc. - 150°F to 190°F
Air compressors can be lubricated or non-lubricated. Non-lubricated air compressors often run hotter than lubricated but taking advantage of this must be carefully applied and well maintained. High operating temperatures are often a path to early operating problems.
There are some potential projects for recoverable energy with HOC that require non-lube air.
4

## Slide 12: The Potential Values of HOC
Provided in the table below are approximate and potential values of HOC in recoverable energy in BTU’s/hour, including probable transport losses.
12
APPROXIMATE VALUES FOR HEAT OF COMPRESSION RECOVERY (PDP 0°F to -5°F) (Includes probable transfer losses) |  |  |  |  | 
Capacity at 100 psig | AIR Cooled Compressor / After-Coolers Estimated Heat Rejection to Cooling Air |  | WATER Cooled Compressor / After-Coolers Estimated Heat Rejection to Cooling Water |  | 
 | Compressor AIR Cooler and After-Cooler Btu/Hr | Heated AIR Maximum Discharge Temperature 120°F / 49°C | Compressor WATER Cooler and After-Cooler Btu/Hr | Heated WATER Maximum Discharge Temperature 125°F / 52°C | 
 |  | Approx. cfm |  | Approx. gpm 70°F | Approx. gpm 85°F
250 | 156,300 | 8,400 | 150,900 | 6 | 10
350 | 208,500 | 8,400 | 200,300 | 7 | 12
500 | 287,700 | 12,000 | 276,700 | 11 | 18
800 | 463,100 | 17,500 | 445,500 | 16 | 27
1,000 | 572,400 | 28,700 | 550,400 | 23 | 39
1,200 | 694,700 | 28,700 | 668,200 | 33 | 56
1,500 | 920,000 | 29,600 | 889,709 | 33 | 56
2,500 | 1,543,000 | 35,000 | 1,543,000 | 49 | 79
5

## Slide 13: Converting BTU/Hour to Annual Electric Cost
How to convert BTU’s/hour into annual electric cost savings?
Here's what you need to know to calculate potential savings:
(measured data from a fixed job)
  System size i.e. scfm capacity and system pressure (2,500 scfm at 100 psig)
  Annual operating hours (6,240 hours)
  Blended electric rate or cost per kWh ($.07/kWh)
  1 kWh = 3,414 BTU’s/hour (constant)
  Total probable recovered BTU/hour at 75% efficiency = 1,157,250 BTU’s/hour 1,157,250 ÷ 3,414 = 339 kW recoverable energy
Total recoverable value of $.07 kWh at 6,240 hrs./yr. = $148,075 savings annually
Every compressed air system has excess heat of compression that is almost certainly recoverable. Look for areas in the plant where it can be utilized – its already paid for!
13
6

## Slide 14: Additional Energy Recovery Opportunities
Other opportunities exist for energy recovery using heat of compression technology.
  Heat of compression stored does not have to be from an oil-free or non-lubricated compressed air – look for specific opportunities.
  There are many successful applications that can implemented with lubricated compressed air primarily by using the heated cooling media to accomplish the final heating at the process. Such as heating specific areas with a dedicated heat exchanger.
14
Methods of Heat Recovery:
Air-cooled units collect all the air in one airstream and then duct the heated air to a desired location. Examples would be like the space heating and heat barrier. Adding booster fans to ensure enough fan capacity to move air without restricting the cooling air flow may be required. Installing this type of ducting work closely with the installer or you could risk damaging the compressor by running too hot.
7

## Slide 15: Case Study: Achieved Savings
The system layout illustrated on the next slide shows two 250hp rotary screw compressors with a 2,500 scfm sized water-cooled refrigerated air dryer. The expected maximum energy recovery was $190,000 annually based on heating the river process water up from the average temperature of 60°F to a nominal 94°F. This takes an energy load off the current electric heater system, because of the varied heat and flow efficiencies. This goal was not met over a 5 year period.
The total annual savings from this project was measured at $128,000 due to much of the pre-cooling effect of the heat reclamation heat exchanger loop on the primary 10-fan closed 60 / 40 polyglycol air-cooled cooling system. Only 8 fans ran most of the summer and 1 -2 fans during cooler temperatures.
15
8

## Slide 16: Case Study: Achieved Savings
Typical Heating Process Water at a Pet Food Plant
9

## Slide 17: A Heat Recovery Application – Lubricated-Cooled Air Compressors
Air Reheater:
Hot cooling oil (190-200°F) or cooling water (130°F) can be used to reheat saturated or high relative humidity compressed air to lower the relative humidity in the pipe. In some applications, this will not only eliminate outside pipe sweating, but also, under proper operating conditions delivering hot, dry air to the process.
This hot air contains more usable energy because the heat raises the pressure with less air volume required and the water vapor is still in the form of a usable gas if it does not cool below the pressure dewpoint (when the vapor then falls out as water).
This has been very popular in sawmill plants where the hot discharge oil from the lubricant-cooled rotary screw compressors (150-200°F) to another heat exchanger and heats the discharge air from the heated oil and delivers lower RH and hotter air to the compressed air system. The hot air in the reheater also pre-cools the heated lubricant, which reduces the heat load on the cooling system.
Typical Lubricant-cooled Compressor Install with Reheater
10

## Slide 18: Charles’ Law and Calculating the Net Savings
18
Charles’ Law:
At constant pressure, the volume of an ideal gas varies directly as the absolute temperature. Absolute temperature °F + 460°Rankin (constant utilized for these calculations) – °F R is also presented as absolute °F
Charles’ Law states that in a confined volume - stored gas will increase in volume in pressure directly proportional to the rise in temperature.
In the example the airline being reheated started at 70°F/95 psig. Adding the 460°R value to the °F makes the absolute F value 520°R. When the reheater was operating these numbers changed to 120°F and 580°R. (520°R ÷ 580°R = 9% increase in pressure which is 95 psig to 104 psig with no change in energy input.
As you peruse deeper into heat recovery the opportunities will astound you!
11

## Slide 19: Common Types of Cooling - Summary
Air Compressors Cooling Impact on Capturing Heat of Compression:
  Air-cooled air compressors – heat of compression trapped into the air to air heat exchanger and cooling system. Heat is available in the cooling air flows will usually discharge cooling air from 5-20°F above the inlet cooling air. To be effective, this cooling air may need thermostatic controls.
  Water-cooled air compressors – heat recovery energy savings and projects are often easier to implement with the heat being well trapped in a controlled water flow. Regardless of the type of air compressor, the maximum expected heated discharge cooling water temperature is about 130°F.
  Oil-injected/coolant-cooled – rotary vanes, screws, scrolls etc. The injected cooling lubricant about 150°F is atomized into the compression chamber absorbing the heat of compression while it is being generated. This generally holds the discharge temperature to about 190-200°F maximum or 165-180°F low.
19
12

## Slide 20: Checking Your Understanding
Check Your Understanding on Heat of Compression Air Dryers – Why do they need oil-free air?
  HOC compressed air dryers require 200°F or more inlet air temperature to deliver optimum operating performance and not have to use extra heating or purge controls.
  The discharge temperature is generally not consistently available with conventional lubricated rotary screw compressors.
  The oil carryover to an desiccant dryer is very harmful to desiccant life and dryer performance.
  The availability of continuous duty non-lubricated compressors such as centrifugals and non-lubricated rotary screws rotary offer a very solid foundations for a long-life oil-free air system.
There is no other dryer technology with lower operating energy costs and inherent low maintenance costs than HEAT OF COMPRESSION, when operating conditions are correct. For most commercial plant air system the HOC is a viable choice when oil-free compressed air is available!
20
13

## Slide 21: Drying Process – Common Types of Heated Full Flow Desiccant Dryers
Note: Will not dry at all above 130°F
All desiccant dryers utilize the process of adsorption – water vapor moves from the saturated compressed air to the surface of the desiccant bead – in their drying cycle.
They will NOT remove liquid water!
14
Notes: Adsorption will not take place at above 130°F
Will only remove water vapor – effective removal of “all liquid condensate” before entry into the drying towers is very important.

## Slide 22: Desiccant Regeneration Process
All desiccant dryers regenerate the wet bed by creating low relative humidity (RH) purge air to remove the water vapor on the surface of the beads.
A common way of doing this is to add heat to increase the RH differential. This is called “heated type” and a heated type of dryer the heat of compression or HOC is “heated” type dryer that utilizes stored heat of compression generated by the compressors or its primary source of regeneration heat. Auxiliary heat is added when conditions call for it.
22
15

## Slide 23: Why Does the Water Vapor Move?
The greater the imbalance the FASTER the transfer!
Fick’s Law of Dispersion:
When there is an imbalance in concentration – (water vapor / relative humidity) the vapor will always move from the high concentration level to the low concentration level to try to equalize regardless of flow direction.
16

## Slide 24: HOC Desiccant Dryer Technology
Compressed 8 Ratios
80°F / 800 acfm Inlet Air / 0 psig (14.5 psia)
250°F / 800 acfm Inlet Discharge Air / 105 psig (119.5 psia)
17
Notes: 800 Cu Ft inlet air 84.5 psia / 8,832Gr/ft3
Intercoolers removed moisture down to about 35gr / 100 Cu Ft – Total moisture delivered 3500 gr.
Regeneration – 100 Cu Ft actual at 105 psig – moisture holding capacity at 250°F 48,200 gr / 100 ft. = 7.3% RH
FICKS LAW!! Moisture moves

## Slide 25: HOC Desiccant Dryer Technology
In most continental USA areas a 200°F discharge temperature in a standard HOC w/o auxiliary heat can delivery at +40°F PDP to a -5° PDP with little or no operating energy costs.
Regeneration
View the Difference!
Drying
18
Notes: The heat of compression supplies the temperature differential to create the “relative humidity” imbalance and allows the removal of the water vapor from the regenerating bed to the air stream.
The air stream goes through the water-cooled aftercooler / separator when the moisture in the air stream is condensed to liquid and removed.
The air stream then goes to the drying tower where all the discharge air is dried and sent to the air system.

## Slide 26: Conventional vs. Heat of Compression
Twin Tower Full Flow Heated Regenerative
Compressed Air Dryer Application Comparison
26
Note the location of the aftercooler
19

## Slide 27: Summary: HOC Dryers
Hot air discharges from the oil-free air compressors and enters the dryer at a very low RH, where it picks up the water vapor.
The hot, wet air then goes to the aftercooler where the temperature is reduced to 100°F or less.
The cool after-cooled air then enters the drying tower where the remaining moisture is removed from the air.
After this cycle is completed, the towers switch and the process is repeated.
NO LOST PURGE AIR!
27
20
Notes: Air moving into the wet tower
Oil-free / 100 psig / 250-350°F with pressure dewpoint of about 160°F
Air to aftercooler
200-300°F saturated air
This air is then cooled to 100°F or less in the aftercooler
The water vapor condenses to liquid and removed by separator and drain, then the air then goes to the drying tower
Leaves the drying tower with a -40°F rated pressure dewpoint at about 100°F temperature with a full flow design
Nominally has the same 8 hour cycle (4 hours drying and 4 hours regeneration) as other heated dryers without the purge air.
There is normally a dewpoint spike or a temperature bump as in all heated dryers, which is a 20-30 minute duration but usually can be well controlled by a dry air cooling cycle and/or inlet air auxiliary cooling during extreme weather.
To always achieve a continuous -40°F PDP or lower may require the use of auxiliary heat and dry air cooling, depending on the demand – under these conditions a full flow HOC dryer will be very economical to run.

## Slide 28: Final Thoughts
This is where we turn the presentation over to one the most knowledgeable men in the country on heat of compression dryers -- Mr. Chuck Henderson of Henderson Engineering.
Chuck and his team have taught me more about desiccant dryers than any group I’ve worked with.
I hope our presentation has taken some of the mystery out of heat of compression and helped clarify this technology for you.
21

## Slide 29
We thank you for the opportunity to present!
We hope you found our presentation informative.
Please contact Air Power USA at (740) 862-4112
if you have any questions.
Air Power USA
Hank van Ormer – Technical Director
(740) 862-4112
22

## Slide 30: About the Speaker
Chuck Henderson
Henderson Engineering Company
Vice President, Henderson Engineering Company
Over 40 years of experience in the compressed air industry

## Slide 31
For your free subscription, please visit www.airbestpractices.com/magazine/subscription.
Chuck Henderson
Henderson Engineering Co., Inc.
Vice President of Henderson Engineering Co., Inc.
About the Speaker

## Slide 32: Maximizing Heat Recovery with Energy Efficient Heat of Compression Dryers
Chuck Henderson
Henderson Engineering Co., Inc.
ChuckHenderson@saharahenderson.com

## Slide 33: Heat-of-Compression Technology
Heat-of-compression technology is rapidly becoming the fastest way to manage a heat recovery project

## Slide 34
To get the greatest benefit of heat recovery, all of the heat-of-compression should be used.
Therefore, regeneration must be full flow.

## Slide 35
Heat is wasted if the valves leak, so selection of components is critical.
Switching valves must be high performance bubble tight.
Air leaks across the valves increase outlet dew point.

## Slide 36: Heat-of-Compression Considerations
Two factors with any mechanical equipment:
1) Basic Design 2) Choice of Components

## Slide 37: Basic Design
Regeneration must be full flow.
Cooling with wet air preloads desiccant and increases dew point.
Inlet heaters add to pressure drop and consume significant energy.
Using 2 aftercoolers doubles GPM.

## Slide 38: Choice of Components
Valves must be high performance bubble tight; leakage across the valve means high dew points.
Multi-port valves leak and should never be used in HOC applications.
Drain traps must work; single traps fail. Where does the water go?
Separators must be efficient at 0-100% flow. Cyclone and centrifugal separators are flow dependent; coalescing separators are not.

## Slide 39: HOC Dryer Sizing Factors
SEVERAL FACTORS DETERMINE THE
POWER, SIZE, AND TYPE OF AN HOC DRYER
Minimum discharge temperature of oil-free air
Maximum inlet flow rate
Minimum inlet pressure
Maximum cooling water temperature
Desired continuous pressure dew point at site conditions

## Slide 40
Notes: 40

## Slide 41
Notes: 41

## Slide 42: Dew Point Demand Often Control Dew Point & Temperature Spike at Tower Switch

## Slide 43: Dryer Operating Costs

## Slide 44: Why Heat of Compression is Popular
1) Virtually no operating cost
2) More reliable than other dryers
3) Guaranteed performance

## Slide 45: Dew Point Integrity to Ensure -40°F/C

## Slide 46: Thank you!

## Slide 47
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions, and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Heat Recovery Project: Heat of Compression Desiccant Dryers
Sponsored by

## Slide 48: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2019 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submit correct answers and notified tomorrow via email and phone.
The next slide will show a statement related to today’s topic that needs to be filled in. You will be provided the first letter of the words as a clue. Please submit your answers in your questions box.
Example
When I think of a beach vacation, I think of _______.
T____
S___ S_____
T___ B___

## Slide 49: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2019 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submit correct answers and notified tomorrow via email and phone.
The next slide will show a statement related to today’s topic that needs to be filled in. You will be provided the first letter of the words as a clue. Please submit your answers in your questions box.
Example
When I think of a beach vacation, I think of _______.
TOWEL
SEA SHELLS
TIKI BAR

## Slide 50: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2019 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submit correct answers and notified tomorrow via email and phone.
Based on the clues below, please submit your answers in your questions box.
When I think of heat of compression desiccant dryers, I think of _______.
H___ R_______
R_______ H________
D__ P____

## Slide 51: Best Practices EXPO Contest
When I think of heat of compression desiccant dryers, I think of _______.
HEAT RECOVERY
RELATIVE HUMIDITY
DEW POINT
Play for a chance to win a FREE Full Conference Pass to the 2019 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submit correct answers and notified tomorrow via email and phone.
Based on the clues below, please submit your answers in your questions box.

## Slide 52: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.
Sponsored by

## Slide 53
Thursday, June 6, 2019 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
Tom Taranto
Data Power Services
Keynote Speaker
June 2019 Webinar Selecting & Sizing Oil-Free Air Compressors
Sponsored by