## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
7 Common Mistakes That Will Ruin Your Air Compressor Efficiency
Ron Marshall, Marshall Compressed Air Consulting
Keynote Speaker

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 6
Introduction
Compressed Air Best Practices® Magazine
7 Common Mistakes That Will Ruin Your Compressed Air System Efficiency

## Slide 7: About the Speaker
Chief Auditor, Marshall Compressed Air Consulting
38 Years with Power Utility
24 Years Technical CA Support
CAC Level 1 and 2 Instructor
International Trainer UNIDO
Ron Marshall
Marshall Compressed Air Consulting

## Slide 9: Coming Up
Seven Common Mistakes
Letting leaks and abuse run wild
Buying a really big compressor for future
Not purchasing a big storage receiver
Saving money by downsizing piping
Solving pressure problems by increasing pressure at the compressor
Over-filtering and drying your air
Cutting corners on your compressor cooling

## Slide 10: Air Compressors Have Poor Natural Production Efficiency
Every 7.5 hp power input to the compressor results in only 1 hp output at the compressed air end use!
Biggest output is heat.
System characteristics affect the input power to flow output ratio
Is compressed air efficient?
Source: Compressed Air Challenge

## Slide 11: Half this energy is wasted
Studies show only 50% actually makes it to the end use:
Leakage - 20 to 30 %
Artificial Demand - 10 to 15 %
Inappropriate Use – 10 to 15 %
How much do you waste?
Source: Compressed Air Challenge

## Slide 12: 1. Letting leaks and abuse run wild
Question: Do your users think compressed air is free?
Makes it easy to justify hooking anything to the system
Leads to high levels of waste and abuse
Solutions: Make users aware of the cost using training
Alter company policy about compressed air use

## Slide 13: 1. Letting leaks and abuse run wild
Question: Do you track your non-productive flow?
Cost of waste unknown
Makes it easy to ignore waste and abuse
No way of identifying what is normal or when changes happen
Solutions:
Measure and record flow during off hours
Set action targets and create awareness
Start leak detection and repair program and actually fix leaks!
Source: VP Instruments
Source: CDI Meters

## Slide 14: 1. Letting leaks and abuse run wild
Training and Awareness:
Leak Tag Boards
CAGI Online Training
Compressed Air Challenge Fundamentals
CAC Compressed Air It’s Not Free session
Leak detector training
Source: Compressed Air Challenge

## Slide 15: 2. Buying a really big compressor for future
Fact: Compressor size can have a large effect on operating costs
Load/unload control:
50 hp compressor at 60% load consumes about 36 kW
75 hp compressor at 40% load consumes around 43 kW
100 hp compressor at 30% load consumes 51 kW

## Slide 16: 2. Buying a really big compressor for future
Solutions:
Measure your flow before buying (CA assessment)
Manage your leaks
Right size your compressor
100 hp compressor at 30% load = 51 kW
2 x 50 hp with one at 60% = 36 kW
100 hp VSD at 30% load = 26 kW

## Slide 17: 3. Not purchasing a big storage receiver
Fact: Tank size can have a large effect on operating costs
Source: Compressed Air Challenge

## Slide 18: 3. Not purchasing a big storage receiver
At 40% flow = 82% kW at 1 gallon per cfm
At 40% flow = 60% kW at 10 gallons per cfm
Consumes 27% less power
Problem: Large tank seldom quoted
Large tank slows down cycle time, better efficiency
Better stabilizes the pressure
Solution: Install between 5 and 10 gallons per cfm total for largest trim compressor.
Install both wet and dry receivers.

## Slide 19: 4. Saving money by downsizing piping
Fact:
Piping restrictions increase operating costs
Power consumption 1% for every 2 psi in extra pressure
Unregulated flow increases 0.9% every 1 psi in extra pressure, more power at compressor
Solution: Ensure piping loss is less than 2 percent across complete system
Only between 20 and 30 fps velocity in any section of main pipe

## Slide 20: 4. Saving money by downsizing piping
Requirement between 20 and 30 fps velocity in any section of main pipe
Means 4 inch for 200 hp 100 psi compressor (1000 cfm)
2.5 inch for 100 hp compressor (420 cfm)
2 inch for 50 hp compressor (240 cfm)
Increase from 2 to 2.5 inch reduces pressure loss by 61%
Increase from ¼ inch hose to 3/8 reduces loss by 70%

## Slide 21: 5. Solving pressure problems by increasing pressure
Fact:
Each 2 psi in higher psi increases power by 1 %
Each 1 psi in higher in psi increases flow about 0.9%
Cost of 20 psi increase on a 200 hp fully loaded compressor running full time = $14,800 for pressure and $6,700 for flow
Total $21,500 in higher costs annually

## Slide 22: 5. Solving pressure problems by increasing pressure
Higher loading loads motor, creates more heat, reduces compressor life
Desiccant air dryers consume more purge at higher pressure
Pressure problems often cause by poor compressor control
High component pressure drop often a problem
Highest pressure loss often in last 30 feet of piping, cheapest to fix

## Slide 23: 6. Over-filtering and drying your air
Fact:
Every filter boosts required discharge psi by 2.5 psi
Two filters cost $3,700 annually for 1000 cfm compressor
Often no need to use coalescing filter for general air use
Proper maintenance is important
Don’t rely on installed differential gauges

## Slide 24: 6. Over-filtering and drying your air
Fact:
Non-cycling 1000 cfm refrigerated dryer = $5,700 per year
Cycling dryer at 50% load = $3,400 per year
Refrigerated vs Desiccant dryer 3 to 4 times more cost
Heatless desiccant fixed cycle = $26,300 per year
Heatless with dewpoint control at 50% = $14,000 per year
Heated with dewpoint control = $8,000 annual

## Slide 25: 7. Cutting corners on your compressor cooling
Facts:
Hot temperatures reduces compressor life and decreases reliability. Increased maintenance.
Excessive temperatures overload the air dryer and may cause air quality problems
If your compressor discharge feels uncomfortably hot to touch then you likely have cooling problems
Solutions:
Always duct the compressor heat away from room
Ensure cooling air/water is cool, clean and unrestricted
Cross ventilate to remove radiant heat
Send heat into plant in winter

## Slide 26: 7. Cutting corners on your compressor cooling
Facts:
About 50,000 btu heat available for every 100 cfm compressor capacity
Compressor heat can displace plant heating
Increase boiler feedwater temperature
Heat process water
200 hp compressor = 145 kW heat rejection
145 kW = $125,000 annual electric heat
145 kW = $22,000 annual natural gas

## Slide 27: 7 ways to fix system efficiency
Tame leaks and abuse with awareness and action
Right size your compressor for present day efficiency
Buy a bigger storage receiver 5 to 10 gallons per cfm
Increase piping size to keep velocity between 20 and 30 fpm
Keep pressure low by eliminating pressure drops
Filter and dry only as required
Well design your compressor cooling, recover heat
Notes: Here is a summary of important points in optimizing compressor system.
Realize that compressed air is expensive and certain negative compressed air characteristics increase the costs.
Leakage wastes energy and decreases system efficiency
Part loading rotary screw compressors can greatly increase the cost of compressed air especially with certain operating modes.
Good savings can be gained by optimizing cycle times by adding storage, reducing pressure drop, and adjusting pressure settings.
These changes lead to elimination of wasteful unloaded run time, especially if VSD mode is used.
Once your system is set up to control the compressor properly doing anything involving reducing flow becomes very effective in increasing efficiency.
The case study success shows the benefit of system optimization not only on energy but on additional system related characterists.

## Slide 28
Questions?

## Slide 29
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
7 Common Mistakes That Will Ruin Your Air Compressor Efficiency

## Slide 30: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2020 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submitted at least 1 correct answer and notified tomorrow via email and phone.
The next slide will show a statement related to today’s topic that needs to be filled in. You will be provided the first letter of the words as a clue. Please submit your answers in your questions box.
Example
When I think of a beach vacation, I think of _______.
T_ _ _ _
S_ _ S_ _ _ _ _
T_ _ _ B_ _

## Slide 31: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2020 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submitted at least 1 correct answer and notified tomorrow via email and phone.
The next slide will show a statement related to today’s topic that needs to be filled in. You will be provided the first letter of the words as a clue. Please submit your answers in your questions box.
Example
When I think of a beach vacation, I think of _______.
TOWEL
SEA SHELLS
TIKI BAR

## Slide 32: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2020 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submitted at least 1 correct answer and notified tomorrow via email and phone.
Based on the clues below, please submit your answers in the questions box.
When I think wasted energy in a compressed air system, I think of _______.
L _ _ _ _ _ _
I _ _ _ _ _ _ _ _ _ _ _ _ U _ _
A _ _ _ _ _ _ _ _ _ D _ _ _ _ _

## Slide 33: Best Practices EXPO Contest
Play for a chance to win a FREE Full Conference Pass to the 2020 Best Practices EXPO & Conference!! This is a $675 value! This contest is open to factory personnel, compressed air distributors, utility incentive programs and engineering firms. Exhibiting and sponsor companies are not qualified. A winner will be randomly selected from those who submitted at least 1 correct answer and notified tomorrow via email and phone.
Based on the clues below, please submit your answers in the questions box.
When I think of wasted energy in a compressed air system, I think of _______.
LEAKAGE
INAPPROPRIATE USE
ARTIFICIAL DEMAND

## Slide 34: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.

## Slide 35
Thursday, April 16, 2020 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
Thursday Webinar How to Correctly Size Vacuum Pumps
Chris Gordon
Keynote Speaker
Blackhawk Equipment
Sponsored by