## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
Air Compressor Master Controls to Prevent Control Gap
Tim Dugan, Compression Engineering Corporation
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Introduction
Compressed Air Best Practices® Magazine
Air Compressor Master Controls to Prevent Control Gap
Sponsored by

## Slide 6: About the Speaker
President and Principal Engineer, Compression Engineering Corporation
Over 25 years of experience in the industry
Sponsored by
Tim Dugan
Compression Engineering Corporation

## Slide 7: Air Compressor Master Controls to Prevent Control Gap
5/21/2020 Tim Dugan, P.E.
Compression Engineering Corporation

## Slide 8: Outline
Definitions
Example System
Problem Definition: Lost in Translation
Solution: Create a Map to Avoid Predictable Problems
Compressor Sizing Options to Avoid Problem
Controls Options to Avoid Problem
Conclusions

## Slide 9: Definitions
Trim: Base:
Unloaded: Turn-down:

## Slide 10: Definitions
Master Control System: Cascade:
Target:

## Slide 11: Definitions
Flow-based
Load-sharing
Hybrid base-trim

## Slide 12: Definitions
Control Gap:
Kinda like Communication Gap

## Slide 13: Example System
Modulating Comp 320 scfm Capacity
VFD Comp 100-315 scfm Capacity

## Slide 14: Example System

## Slide 15: Example System
Happy Place:
  from 100-315 scfm:
  from 420-635 scfm:
But what happens between 315 to 420 scfm?
  Not happy … why?

## Slide 16: Problem Definition: “Lost in Translation”
Flow and Pressure – Two Different Languages:
The air system speaks the “Flow language”.
Controls speak “Pressure language”.
Flow is translated to Pressure and vice-versa by …Physics.

## Slide 17: Problem Definition: “Lost in Translation”
The Conversation Starts Civil, Flow = 200 scfm
VFD in sweet spot, base-load in standby
System whispers: “More air please”
System whispers again: “Less air please”
Physics translation is clear: Pressure changes slowly
VFD’s answer: slight speed change

## Slide 18: Problem Definition: “Lost in Translation”
Another Person Intervenes in the Conversation at 320 scfm
VFD at full capacity & base-load in standby
System whispers: “More air please”
Physics translation is clear: Pressure drops slowly
VFD is unresponsive – already at full speed.
Master controls takes over: starts base compressor

## Slide 19: Problem Definition: “Lost in Translation”
An Argument Erupts:
Starts With the First Conversation (VFD control)
Ineffective, Bounces Back to the 2nd Conversation (Master Controller Control)
Ineffective, Bounces Back to the First Conversation (VFD control)

## Slide 20: Problem Definition: “Lost in Translation”
Root Causes of Problem:
No “dictionary”
No “map”
No “algorithm”

## Slide 21: Problem Definition: “Lost in Translation”
Is There Hope?
Can all Control Gap problems be solved?
Can they sometimes be avoided?
Can they be predicted?
Are there effective algorithms for unavoidable gaps?

## Slide 22: Understand the Dictionary: PV Physics
Anticipate Pressure Rate of Change:
A simple formula:
1 delta scfm on 1 ft3 will cause a 1 atm/min pressure rate of change.
Starting base comp: 320 scfm delta on 1000 gal => 35 psi/min, 0.5 psi/sec
Set Timers and Pressure Differentials Accordingly

## Slide 23: Flow Measurement: Predicting Problem Areas
Develop a Reliable “Total Flow” Metric
Direct flow measurement preferred
Meter type?
Location?
Comprehensive
Load-unload smoothed out

## Slide 24: Create a Flow Map to Predict Problem Areas
Develop Compressor vs Total Flow Chart
Determine control strategies in each
Use actual capacities w- your flow meters
Identify Control Gap

## Slide 25: Solve Problem by Compressor Sizing
To Avoid Control Gap – “You’re Gonna Need a Bigger VFD Compressor!”
Make the VFD >= 1.5X the size of the Base.
Option: Get a Smaller Base Compressor, <= .66 x VFD Compressor

## Slide 26: Solve Problem by Controls Tuning
Target when VFD in Speed Range
Cascade in Control Gap.
Force the VFD to be Trim, start/stop (or load/unload) at min speed.
Can be done by forcing the VFD unload point lower.
Smart adaptive controls can change set points in the problem areas.

## Slide 27: Summary
Optimal: VFD swing capacity larger than base, target controls.
If not, Control Gap will result.
Have a reliable total flow metric & strategy chart to predict where the Control Gap will be.
Changing size of compressor(s) is the most robust way of eliminating the problem.
If compressor change is not possible, automation needs to know when Control Gap is coming.
Automation should revert to Cascade control in those gap areas.

## Slide 28: About the Speaker
CEO, VPInstruments
> 20 years experience
VPInstruments offers industrial clients Energy Management Solutions for compressed air, technical gases as well as other utilities
Sponsored by
Pascal van Putten
VPInstruments

## Slide 29: Energy savings at a glass factory
By insertion flow meters combined with compressor controls
Notes: Welcome at this presentation about energy savings at a Dutch glass factory. VPInstruments has been involved with this glass factory for many years, where we have supplied 20 flow meters over all the years for their compressed air system measurements. It was Stork who built upon those flow meters and introduced significant energy savings at this factory.
First some general remarks about compressed air usage in glass factories

## Slide 30: Compressed air in glass industry
Critical utility for production
Up to 30% of electricity costs
Savings potential up to 50%
Pressure band width is critical:
  Quality of glass
  Continued production
Adjustable
speed drives
Chart: 
| reducing air leaks | Overall system design | Recovering waste heat | Adjustable speed drives | All other measures
 | 0.42 | 0.12 | 0.1 | 0.1 | 0.26
10%
26%
42%
12%
10%
All other
measures
Overall
system
design
Recovering waste heat
reducing air leaks & optimize supply
Major energy saving measures
Notes: Compressed air in glass important utility. Used to drive glass blowing machines and to blow liquid glass into moulds.
In glass factories compressed air can take up to 30% of the electricity bill, as to 10% compared to the entire industry.
With a savings potential up to 50% , savings can be enormous for glass factories.
In addition, the band width of the pressure level in the compressed air system is critical. Too high or too many pressure fluctuation and e.g. bubbles are formed in the glass. Too low, machines can drop to a standstill. Any pressure reduction results in significant savings, as 14.5 psig pressure reduction is 7% savings.
Niet grafiek gaan uitleggen! Kost teveel tijd! Gewoon plaatje

## Slide 31: Compressed air system lay out
Low pressure @ 49 psi av. consumption 9.400 SCFM
High pressure @ 84 psi av. consumption 13.000 SCFM
Notes: This Dutch glass factory produces bottles for the Netherlands, Belgium and Luxembourg with a production of 1 billion bottles of green and brown glass annually. Their compressed air systems exists, like other glass factories, of a Low pressure and high pressure compressed air network.
Dick: kunnen we nog iets zeggen over waar het HP en LP network global voor gebruikt wordt? LP: Blow molding. HP: Transport, Filters, in the IS machines (instrument air). Dew point: LP = Fridge dried. HP = Desiccant dried

## Slide 32: Compressor room lay out - before
2 x Centrifugal
Each 4.340 – 3.280 SCFM
8 x Screw
Each 1.240 SCFM
Centrifugal
7.650 -5.590 SCCFM
Centrifugal
5.530 -3.770 SCFM
LP Pressure
49 psi
+/- 9.400 SCFM
HP Pressure
84 psi
+/- 13.000 SCFM
Regulator
emergency valve
84 to 49 psi
Notes: Situation before. The centrifugal compressors were all individual and not centrally controlled, nor connected to the screw compressor controls.
So just one example: In the LP pressure line: consumption by average was: 9400 SCFM. The left compressor was running full load. The left was then running for its minimum, which is 3770 SCFM. So almost1800 SCFM was blown off, just pure energy loss.

## Slide 33: Before implementation
High pressure system:
Both centrifugal air compressors always running full load.
Screw compressors started @ 84 psi: resulting in pressure fluctuations: 81,75..85,40 psi.
Unloaded hours on screw compressors.
Emergency regulator: only activated when pressure drops in LP system to 46,7 psi.
Flow meters installed in 2013 + only for indication: observe flow/HP/h consumption.

## Slide 34: Before implementation
Low pressure system:
LP compressor: maintaining 49 psi in main header.
Compressors running without communications but on same system pressure transmitter.
No loadsharing.
Occasional blow off.

## Slide 35: How do we add value
Install & connect flow meters
Install booster compressor
Modify regulator valve
Install Master controller
Energy savings !

## Slide 36: Compressor room lay out - improvements
Booster Compressor
49 to 84 psi
2.354 SCFM
Notes: Booster is “nice to have” keeps LP constant P, as many possible via the booster. If booster in trip or service, load sharing on the LP compressors. Very flexible system, fully automatic.

## Slide 37: Requirement from customer
LP system is most critical. Pressure 49 psi. Dev. +/- 0.7 psi.
Energy savings @ maximum when booster compressor is running full load.
Energy savings @ maximum when screw compressors are only running full load.
  (implemented at phase 2)
When one of the low pressure units trips actions:
  Booster should unload and stopped.
  Screw compressors starts up depending on the needed flow.
  Emergency regulator valve should open to maintain the low pressure.
Notes: Drukband op gegeven door O-I. afh kwaliteit van de flesjes – afh van drufluctuaties
Druk onder 3 bar bij LP luchtbellen in glas.

## Slide 38: 1st Phase implementation results
Installation centrifugal booster : capacity 2.354 SCFM.
  Booster feeds the HP system: 2 screw compressors are not needed
Rebuild LP + HP compressors to a new control system including load sharing.
Rebuild existing control from emergency control valve to Stork controller.
Use flow meters to control demand to booster.
Notes: With the excisting low pressure air demand and running with the two units there is around 4000Nm3/hr. availlble to feed the booster compressor. In this case the low pressure units are running full load.
The booster feeds the high pressure system, and 3 oilfree screw compressors are not needed.
With the flow meters we measure how much are on the low pressure system is availlable to feed the booster. If the demand on the low pressure system increase we use the flow meters input to decrease the load on the booster. P lower @ Max flow  Reduce booster.

## Slide 39
Energy savings :
294 kW/hr.
Just the beginning….
Energy savings :
294 kW/hr.
Just the beginning….
Notes: 10:34: Stork controls were activated. You can see the difference in fluctuations. Savings thusfar: 150K USD per year! Also allows pressure reduction to 5.1 bar continuous => Addiitnal savings ~ 1800 kW * 3% ~ 40 kW additional. Also, opens opportunity to shut down cooling of screw compressors. So the treasure hunt continues! ;-)
2nd phase is implemented as we speak. Target: 520 kPa pressure level in HP part. Another 2 to 3% energy savings on total consumption. Furthermore the excisting flow meters will be used for the master control system. With the input of this flow we will calculate if a screw compressor should be started and loaded into the system.
With the flow meters the master controller calculates if a screw compressor can be shut down when the demand fits into the capacity of the centrifugal compressors.

## Slide 41
info@vpinstruments.com
www.vpinstruments.com
VPInstruments

## Slide 42: About the Speaker
Product Manager, BEKO Technologies
Sponsored by
Josh Borrego
BEKO Technologies

## Slide 43: Holistic approach to compressed air system measurement and control
Compressed Air Best Practices Webinar
May 2020
Josh Borrego, Product Manager
BEKO Technologies Corp.

## Slide 44
Overview
Why are we measuring?
What does it mean?
What do I do with it?
Notes: To a person who has never flown before, the cockpit shown seems like a complex maze of readouts, buttons, and levers.
But to an experienced pilot, these readouts allow them to make important decisions and react properly to them. The implementation of sensors and controls has proven effective in creating one of the safest and efficient mode of travel we currently have.
In this presentation, I would like to help others understand why we are measuring compressed air readings,
What the readings mean by describing some of the more common sensor types,
Some practical examples of what to do with the readings.

## Slide 45
Why are we measuring?
Think about which one you would like to take on a 500 mile road trip in a day.
Notes: Lets start with a quick, more common example. We have 2 vehicles shown in the example. Think about which one you would like to take on a 500 mile road trip in a day. Now think about the reason why most of us would choose the newer vehicle.
What is the difference between these 2 vehicles?
- Performance
- Reliability
- Efficiency
- Safety
How did the high performance vehicle achieve these benefits over the older vehicle?
The implementation of sensors for viewing information and driving controls

## Slide 46
Why are we measuring?
PERFORMANCE
RELIABILITY
What value does implementing quality measurement and control bring to the compressed air system?
EFFICIENCY
EFFICIENCY
SAFETY

## Slide 47
Why are we measuring?
What value does implementing quality measurement and control bring to the compressed air system?
EFFICIENCY: Monitoring and controlling the system can ensure that all of the equipment is operating to its peak efficiency. Performance is validated
SAFETY: The use of sensors and controls alerts you to the system operating outside of safe values. Also, monitoring the system assures the final product will not be negatively effected by the quality of the compressed air
PERFORMANCE: Enabling the maximum quality output for the compressed air system. Allows benchmarks to be set for your facility to know exactly what your capabilities are.
RELIABILITY: By utilizing all of the data avaible, the ability to set up predictive maintenance leads to the avoidance of costly downtime

## Slide 48
Oil vapor content
Pressure
Common sensor overview
What information do I need?
Flow
Temperature
Pressure
Dew Point
Notes: The information needed to be gathered can vary among different installations due to different quality and performance requirements.
It is important to evaluate your installation, determine what is important information as it pertains to your or your customer’s installation in order to ensure the information gathered will serve a purpose.

## Slide 49
Sensor descriptions
Pressure:
Find system issues. e.g. high pressure drops
Set a baseline then use to evaluate service requirements on air treatment.
Calculate cost of air treatment
Set alarms to enable quick reaction to system issues
Pressure Dew Point:
Set a benchmark for air treatment performance
Validate air treatment performance is up to quality requirements
Set limit values to alert if exceeded
Notes: Pressure:
Pressure sensors can be used for diagnostics with pressure drops. Say, if a drain fails on refrigerated dryer or a filter, the pressure drop will increase. You can use the sensor to generate a signal to alert service personnel.
When evaluating pressure drops, you can set a baseline and use the pressure drop to determine if filtration needs to be changed. This is condition based monitoring and can help alleviate downtime and save money.
Use the readings combined with the CAGI cost of pressure drop calculator to better understand the cost of treating your air.
Dewpoint:
Use to set benchmarks for compressed air treatment and evaluate their operation continuously.
Use the sensor to drive controls and protect the end product.

## Slide 50
Sensor descriptions
Temperature:
Verify the operation of air treatment e.g. aftercoolers
Verify ambient conditions to ensure it is within the operating limits of nearby equipment
Use to alert if the compressed air temperature falls below the dew/frost point value
Flow:
Set a benchmark for compressor flow performance.
Calculate consumption and velocity of compressed air
Set limit values to alert if exceeded
Determine if an air system has leaks
Notes: Temperature:
Verify the operation of air treatment such as aftercoolers. You can use this information to predictively set maintenance for cleaning. The sensor being placed in the air stream between the compressor and air dryer can also be good to base alerts off of so you ensure the inlet temperature does not go above the ratings of the dryer.
Measure the ambient temperature to ensure your it is within the operating limits. All equipment has operating temperature ranges. Monitoring, alerting, and controlling will work towards preventing downtime.
Flow:
Setting a benchmark for compressed air flow at your facility will enable you to set limits that should not be exceeded. Based on these benchmarks you can utilize the flow sensor to control different devices or alert personnel of potential issues.

## Slide 51
Sensor descriptions
Oil Vapor monitoring:
Validate oil free operation
Use for control in order to protect sensitive processes
Set limit values and alert if exceeded

## Slide 52
Other information to consider
What other information may be available to drive controls or alert operators to issues?
Notes: Most compressed air equipment has sensors built in to drive the individual piece of machinery. Many pieces of equipment have already built in methods for external communication that are under utilized. When choosing equipment, it is important to ask, “how can I get the most out of this investment?”
Can the internal information be communicated external of the equipment to view or drive other controls?
Sensor readings
Alarm contacts
Equipment status
Can external information be communicated to the equipment to assist in driving controls?
Remote start stop
Compressor synchronization

## Slide 53
Measurement processing
Local display /
View only
Data logging and control
via dry contacts
Information sent to building
system or other for further
evaluation and control
How should we gather and process the information?
Compressed air >
Compressed air >
Sensor

## Slide 54
Measurement processing
View only:
Indication to operators.
Data logger:
Indication to operators.
Can be used to drive simple controls.
Generate alarm signals.
Data log values for historical
comparison, cost calculations
or troubleshooting.
Building management systems or other:
Functionality based on specific systems.
The method of how the information is digested and used
is based on the individual needs of the process and plant.
Some basic descriptions of the type of display and use are
shown here.

## Slide 55
Practical examples
Measuring pressure drop, what are the benefits?:
Calculation of air treatment cost
Benchmarking performance of air treatment.
This then allows for scheduling maintenance on performance and not time.
Troubleshooting and alerts:
Sudden high pressure drops can mean a few things such as excessive flow rates, drain malfunctions, and air treatment issues.
Verify pressure is meeting requirements at the process

## Slide 56
Practical examples
Measuring Flow, what are the benefits?:
Benchmark entire system performance
Calculate cost based on consumption
Troubleshooting and alerts:
Find if your system has costly leaks.
Identify potentials for process improvement to increase efficiency.
SCFM
0
100
No production
Air still being
consumed
Leak rate = savings potential
Time

## Slide 57
Practical examples
Measuring Temperature, what are the benefits?:
Ensure that aftercoolers are working properly and clean
Ensure load conditions for air treatment are met and not exceeding limitations. Both ambient and
compressed air inlet.
Limit of building
Use for controlling auto switch over of dryer type when limitations are weather dependent.
Outdoors

## Slide 58
Practical examples
Drain alarm
contacts
Compressor synchronization
Utilizing built in control signals and alarm relays, what are the benefits?:
Compressor synchronization ensures the desiccant dryer does not consume purge when there is no compressed air demand
When used with integrated Pressure Dew Point control, large savings potentials can be realized as well as confirmation of performance
Using built in alarm contacts for drains can alert and protect downstream equipment from being overloaded or damaged

## Slide 59
Support
Questions, Guidance, or Advice …. We are here to help
BEKO TECHNOLOGIES CORP.
900 Great Southwest Pkwy SW | Atlanta, GA 30336
Phone + 1 (404) 924-6900 | Fax + 1 (404) 629-6666
www.bekousa.com

## Slide 60
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Air Compressor Master Controls to Prevent Control Gap
Sponsored by

## Slide 61: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.
Sponsored by

## Slide 62
Thursday, June 18, 2020 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
June Webinar VSD Air Compressor Installation Guidelines
Loran Circle
Keynote Speaker
Circle Training & Consulting