## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
Sponsored by
Compressed Air Condensate Drain Selection and Oil/Water Separation
Loran Circle, Circle Training & Consulting
Keynote Speaker

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Sponsored by
Introduction by Rod Smith, Publisher
Compressed Air Best Practices® Magazine
Compressed Air Condensate Drain Selection and Oil/Water Separation

## Slide 6: 2019 Best Practices EXPO & Conference

## Slide 7: 2018 Best Practices EXPO & Conference

## Slide 8: About the Speaker
Senior Consultant, Circle Training & Consulting
Over 45 years of experience in the compressed air industry
Certified AirMaster Plus by Department of Energy
Sponsored by
Loran Circle
Circle Training & Consulting

## Slide 9: COMPRESSED AIR CONDENSATE MANAGEMENT
Loran Circle
Thursday November 15, 2018

## Slide 10: Condensate Disposal
There are basically three types of disposal
To a municipal sewage treatment plant which will be governed by your local water district.
To storm drain, tributaries, or wetlands which in most cases will require a state or federal permit. If you currently have effluent water discharge from your plant, the condensate disposal would generally come under that permit.
To ground, which is not allowed in most all cases. It eventually could be washed off to storm or into the wetlands causing groundwater contamination

## Slide 11: Discussion Points
How does condensate happen and why is there oil entrained in the condensate?
For this discussion we will mainly be referring to oil carryover in condensate used in oil flooded rotary screws, rotary vane and reciprocating air compressors
In Centrifugals and Oil Free Screw air compressors there is no oil used in the compression chambers, thus usually do not need oil/water separation systems.
Condensate contaminates the compressed air system causing corrosion, equipment failure and product spoilage - It must be removed using filtration and drying methods
Removal from the compressed air system creates new problems
Oily condensate discharged into the environment kills plants, fish & animals.

## Slide 12: Condensate and Oil
Air is taken into the inlet of the air compressor containing moisture in vapor form (humidity)
When introduced into the compression chamber on rotary screws, the vapor mixes with the oil
On reciprocating compressor the oil makes contact with the air by seepage past the rings on the piston. The longer between ring changes, the higher the oil content
After compression takes place, the air/lubricant on rotary screws is separated by a separator. The oil is recirculated, and the air is sent to an aftercooler to drop the temperature causing condensation
The condensate is then trapped out of the system and discharged to an Oil/Water Separator before being sent for disposal.

## Slide 13: Drains and Traps
Plugged traps and malfunctioning drains are the single largest cause of water in the compressed air system!

## Slide 14: Typical Compressed Air System With Refrigerated Dryer
Used with permission from the Compressed Air Challenge

## Slide 15
Calculation Chart for Determining Amount of Condensate in Air

## Slide 16: Functions of a Lubricant
Control temperature in the air compressor
Form a seal to decrease slippage between the screws
Control friction between the screws or the piston and cylinders
Control wear of both type air compressors
Control corrosion
Remove contaminants
Lubricate bearings

## Slide 17: Sample MSDS for Polyalphaolefins

## Slide 18: Lubricant Types Affect Type of Oil/Water Separators Used
Let’s break down the different types of lubricants that effect the type of oil/water separator needed for your application. On the MSDS sheet the manufacturer will list the specific gravity of the lubricant.
This is important in choosing the right oil/water separator for your application.
It is important to know the Specific Gravity of your lubricant found on the MSDS sheet
Water is the base specific gravity and is 1.0
Diesters (Reciprocating air compressor oils) = .93
Petroleum Based .87
Polyalphaolefins .83-.90
Polyolester lubricants .97-1.0
Polypropylene Glycols sp. 0.9827
Silicone based lubricants 0.97
The lower the specific gravity, the easier it is to use flotation type Oil/Water Separators

## Slide 19: How Poor Maintenance Affects Lubricant Levels in Condensation
Quality of maintenance of the equipment. Without proper maintenance, the oil carryover into the condensate can increase many times over.
Make sure your oil/water separator is changed at proper intervals to avoid saturation. This will add to the levels of contaminants in your condensate.
Check the oil return line screen or filter. This picks up oil passed through the separator and returns it to the inlet of the air compressor. A plugged oil return line will add to the carryover levels. Also placement of oil return line inside of the separator is important. If the pick up line is too low or too high, it may not be effective in removing excess oil.
Aftermarket parts can effect the carryover of oil. Manufacturers design their oil separation system around their parts. Using other parts not specifically designed for your air compressor, could cause oil carryover to increase.

## Slide 20: How Air Compressor Controls Affects Lubricant Levels in Condensation
Load/No load controls could effect the oil carryover if a receiver tank is not sized properly causing the air compressor to short cycle rapidly.
If modulation controls are not set properly, the air compressor can short cycle increasing oil carryover
Variable speed drive air compressors can increase oil carryover in cases where the air compressor is operating on a minimum speed level
All of these factors need to be considered when sizing an oil/water separator

## Slide 21: What You Need to Determine
Is your facility covered under a state program or national program?
Are you discharging condensate to Sewer, Stormwater or Tributary?
What is the type of lubricant you are using?
What are the levels of contaminant in the condensate?
What are your local water treatment regulations?
What options are available for condensate cleanup prior to discharge?

## Slide 22: So What To Do?
First is to determine your site conditions
Is your plant on a municipal system?
Does your plant have its own water treatment system?
Which regulatory department does your plant’s location fall under?
Find out what levels of contamination are allowed for your location
Have your raw condensate tested by a laboratory or oil/water separator manufacturer’s test kit.
Many of your oil/water separator suppliers provide this service

## Slide 23: Before Starting Your Search for the Right Oil/Water Separators
Get the manufacturers MSDS sheet for the lubricant
What is the type of lubricant?
Is my lubricant biodegradable?
(*Caution: Biodegradable lubricants can still be toxic and difficult to treat by waste water facilities. Check with local authorities when disposing of these fluids.)
What is the approximate oil carryover of the air compressor?
Where is the final destination of the condensate?
What are the local regulations regarding levels of contaminants within the condensate?
How much condensate is being disposed of?

## Slide 24: Types of Oil/Water Separators
Skimmer types
Absorption types
Filtration types
Flotation types

## Slide 25: Things to Know About Condensate
Regulations affecting condensate levels are different depending on your plant location.
Some the regulations come under the states jurisdiction
Others come under the federal jurisdiction
Once you determine what jurisdiction your location is under, check what your local municipality requires to dispose of condensate into their sewage system
If you are not under a municipality, then you are probably subject to regulations of discharge into wetlands and tributaries and most states require a study and application for a permit

## Slide 26: In Closing
Do not send condensate directly to ground at any time even with an oil/water separator
Find which agency your are governed by
Determine the amount of carryover in ppm and what is allowed in your location
Talk to your local supplier and get your water tested and the MSDS from them
Even though the local supplier could be knowledgeable, your plant is responsible for any contamination
Make sure you check and document your local requirements

## Slide 27: Thanks for Attending
Mark Your Calendars
Don’t forget to register or get your booth reserved
for 2019 Best Practices EXPO & Conference
October 13-16, 2019
Nashville Music City Center
www.cabpexpo.com
Loran Circle
Certified AirMaster Plus
Sales, Air System Design, and Maintenance Training
for The Compressed Air Industry
Pearland, Texas
832-906-0469

## Slide 28: About the Speaker
Russ Jones
BEKO Technologies
Regional Sales Manager, BEKO Technologies
Over 20 years of experience in the compressed air industry

## Slide 29
COOLING
SEPARATION
DRAINING
STORING
COMPRESSION
DRAINING
DRYING
DRAINING
FILTERING
DRAINING
A Chain is Only As Strong As Its Weakest Link
| General Info – The Compressed Air Chain
Reliability is KEY for the CHAIN

## Slide 30: | General Info – Drain Types
electronic controlled drain with capacitive sensor
timer controlled
solenoid valve
level controlled
timer controlled
electronic
mechanical
mechanical float drain
automatic
drain
manual
drain

## Slide 31: | General Info – Condensate Drain Types

## Slide 32
Next up: Electronic Zero Loss Drain Function

## Slide 33: | Electronic Zero Loss Drain Function

## Slide 34: | Electronic Zero Loss Drain Function

## Slide 35: | Electronic Zero Loss Drain Function

## Slide 36: Electronic Zero Loss Drains
Indicates when service is due
Indicates all alarm types
Ability to unclog and unjam
Dry contact for further feedback
Why is Power Important?

## Slide 37: Electronic Zero Loss Drains | Advantages
Saves Energy
Return Of Investment <12 months
Noise reduction
No Oil Vapor in the compressor room
No Air Loss

## Slide 38: Electronic Zero Loss Drain Maintenance |
Quick Replacement Service Units
Good for 1,000,000 Cycles or 8,000 Hours
Replaces all moving parts and built in strainer
Strainer installed before drain?
No!

## Slide 39
Next up: Electronic Zero Loss Drain Application

## Slide 40: Electronic Zero Loss Drain | Application
Easy to Use Sizing Charts Available
Identify Air Flow to Drain Location
Determine Drain Location in System
Confirm Operating
Parameters of Drain

## Slide 41: Electronic Zero Loss Drain | Application
ROI Calculator Available

## Slide 42: Electronic Zero Loss Drain | Installation

## Slide 43: Electronic Zero Loss Drain | Installation

## Slide 44: Oil Water Separators
So where does all that efficiently drained condensate go?
And is it just water?

## Slide 45: Oil Water Separators| General Info
On average, how much oil does a 100 HP compressor pass each year?
Conservatively about 10 gallons per year!

## Slide 46: Oil Water Separators | General Info
Fact: It takes 2.5 drops of oil to contaminate one gallon of water…
Fact: 1 gallon of oil would contaminate about 1 MILLION gallons of water…
A 100 HP Compressor is capable of contaminating 10 MILLION GALLONS OF WATER PER YEAR
Notes: Contamination level considered 10ppm our higher.

## Slide 47: Oil Water Separator | General Info
Where should the condensate and oil go after it is discharged from a drain?
or
or

## Slide 48: Oil Water Separator | Function
Depressurization Chamber
Main Cartridge
(Polishing)
Pre-Filter
(Floating)

## Slide 49: Oil Water Separator | Function

## Slide 50: Oil Water Separator | Maintenance

## Slide 51: Oil Water Separator | Maintenance

## Slide 52: Oil Water Separator | Maintenance
Clean and Easy to Change Cartridges
Landfill Compliant

## Slide 53
Identify type of compressor
Identify type of oil
Match up to HP or SCFM
Apply climate zone correction factor
Oil Water Separator | Application and Sizing

## Slide 54: Oil Water Separator | Application and Sizing
Cartridge Life Expectancy and Climate Zone Correction Factors

## Slide 55: Oil Water Separator | Installation

## Slide 56: Oil Water Separator | Installation

## Slide 57: Oil Water Separator | Installation

## Slide 58
THANK YOU!

## Slide 59
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions, and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Sponsored by
Q&A
Compressed Air Condensate Drain Selection and Oil/Water Separation

## Slide 60: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.
Sponsored by

## Slide 61: 2019 Best Practices EXPO & Conference

## Slide 62: 2019 Webinar Series
Proper Installation & Sizing of VSD Air Compressors – January 24, 2019
Visualizing KPI’s: Specific Power, Flow, Pressure, Dewpoint – February 28, 2019
Air Quality Specs: ISO 8573.1 & the Safe Quality Foods Standard – April 4, 2019
Selecting & Sizing Heat of Compression Desiccant Dryers – May 16, 2019
Selecting & Sizing Oil-Free Air Compressors – June 6, 2019
Control Strategies for Multiple VSD Air Compressors – July 18, 2019
Piping and Storage for Compressed Air Systems – August 22, 2019
Air Compressor Lubrication & Maintenance – December 12, 2019
Register for free at
www.airbestpractices.com/magazine/webinars