## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees on within 2 days.
Measuring Dew Point for Process Safety, Quality and Efficiency
Ron Marshall, Marshall Compressed Air Consulting
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Introduction
Compressed Air Best Practices® Magazine
Measuring Dew Point for Process Safety, Quality and Efficiency
Sponsored by

## Slide 6: About the Speaker
Consultant MCAC
38 years with Power Utility
24 years Technical CA Support
CAC Level 2 Instructor
International Trainer UNIDO
600+ projects completed
Sponsored by
Ron Marshall
Marshall Compressed Air Consulting

## Slide 7: Wanted Energy Wasters

## Slide 8: Coming Up
What is dew point?
Needs in CA – Air Quality
What happens if quality not maintained
Why measurement is important
Dryer controls – EE concerns
Problem examples regarding dew point

## Slide 9: Why is dew point important in compressed air?
The dew point is the temperature to which air must be cooled to become saturated with water vapor
When cooled further, the airborne water vapor will condense to form liquid water
When air cools to its dew point through contact with a surface that is colder than the air, water will condense on the surface

## Slide 10: What is pressure dew point?
The term “pressure dew point” is encountered when measuring the dew point temperature of gases at pressures higher than atmospheric pressure
It refers to the dew point temperature of a gas under pressure. This is important because changing the pressure of a gas changes the dew point temperature of the gas - Vaisala

## Slide 11: Dew point compression and drying
Source: CAGI Handbook

## Slide 12: Dew point compression and drying
Source: CAGI Handbook

## Slide 13: Dew point classes ISO 8573-1
Source: CAGI Handbook

## Slide 14: Negative effects of moisture in compressed air
Washing away required oils
Rust and scale formation within pipelines and vessels
Increased wear and maintenance of pneumatic devices
Sluggish and inconsistent operation of air valves and cylinders
Malfunction and high maintenance of control instruments and air logic devices
Product spoilage
Rusting of parts after sandblasting
Freezing in exposed pipelines during cold weather
Further condensation and possible freezing of moisture in mufflers whenever air devices are rapidly exhausted
Source CAGI Handbook
Source: CABP Magazine

## Slide 15: Growth of microorganisms
“To support microorganism growth, it is necessary to establish conditions that will permit organism reproduction. All microorganisms require the following to remain viable and grow on culture media:
Nutrients
Proper pH
Appropriate temperature
Gasses
Moisture
Source: Atlas Copco compressed air and microorganisms white paper
Source: CABP Magazine

## Slide 16: Things are not always the way they appear

## Slide 17: Question: What is the actual dew point of this plant?

## Slide 18: Panel displays temperature not dew point
Source: Atlas Copco

## Slide 19: Desiccant air dryers consume costly compressed air
Source: Atlas Copco

## Slide 20: Dew point issues
Instruments on refrigerated dryers do not measure actual dew point, output could be different
Dew point controls on desiccant dryers:
  Incorrect readings may cause air quality issues
  Incorrect readings may cause air dryer inefficiency
  Example 1,000 cfm air dryer in fixed cycle 15% = 150 cfm
  At light load of 50% purge = 30% of actual
  Properly working dew point control could save up to 75 cfm
  At $0.10 per kWh saves $13k per year

## Slide 21: Example dew point problems – Refrigerated Dryer
Food plant with refrigerated areas
Audit showed dew point spikes during day production hours
No alarms on dryer
Constant problems with moisture in air, testing revealed contamination
Overheating due to poor ventilation and minimal size of dryer
Solution fix room temperature
Install dew point probe and alarm

## Slide 22: Example dew point problems – Heated Dryer
Dryer was constantly cycling, would never reach -40 switching point
Reading checked against portable dew point probe and found in error
Malfunction in dryer cooling was damaging probe
Replaced probe and operation returned to normal

## Slide 23: Example dew point problems – Heated Blower Dryer
Poor dew point in plant
Dryer constantly running
Compressor coolers plugged
Dryer over temperature
Excessive moisture in air
Dew point probe flooded and out of calibration
Cooling repair and probe recalibration

## Slide 24: Example dew point problems – Dual dryers
Poor dew point in plant
Refrigerated areas in plant
Dryer 1 frozen on right side dry
Dryer 2 over temperature
Excessive moisture in air
Excessive purge flow during light loads
Dryer repair and probe calibration

## Slide 25: Summary
Dew point not always what is seems
Refrigerated dryers need probes
Secondary probes on desiccant
Proper calibration schedule
Hook up alarms
Make sure personnel are trained to recognize bad readings
Handheld or data logger connected probe useful for CA auditing
Source: Vaisala

## Slide 26: About the Speaker
Business Development Engineer, VAISALA
Over 16 years of experience
Justin.Walsh@Vaisala.com
Sponsored by
Justin Walsh
VAISALA

## Slide 27: Topics
Energy Efficiency with Dew Point Control
Dew Point Sensor Technologies and their Performance
Selecting the Right Instrument for your Operation
Maintenance & Calibration Preserves Efficiency

## Slide 28: Vaisala
January 1997
Vaisala launched the first ever polymer sensor for dew point measurements. DRYCAP® technology is now used in a wide variety of industrial applications.
80+ years of experience providing measurement products and services
Trusted supplier of instrumentation to protect processes and explore the unknown
Measurement solutions for indoor and industrial environments ensure, product quality, cost/energy efficiency and personal safety and wellbeing

## Slide 29: Compressed Dry Air Energy Demand
Food Safety
Hospitals
Product Quality
Protect Capital Equipment
7-8 times More electricity to produce power
Leaks account for big losses
Thermal Challenges
  Creation
  Storage
  Use
Importance of Accuracy
Energy Demand

## Slide 30: Increased Efficiency with Dew Point Demand Switching
Dew Point Demand Switching for a Heatless Desiccant Dryer (HDD)
Cycle Timed Switching:
-40 (Td), 1200 cfm, 250hp
15% Purge Flow (180 cfm) / Every 5 min
350cfm = min, 900 cfm = avg, 1080 cfm = max
261+ kWh / year
Savings Example
Td Demand Switching:
-40 (Td), 1200 cfm, 250hp
15% Purge Flow (180 cfm) / 5 min then STOP
> 1200 cfm = desiccant bed lasts longer
32% reduction in operating costs (82k kWh/year)
Image Credit: SPX Flow Hankison

## Slide 31: Dew Point Sensing Technologies
Chilled Mirror
Metal (Al) Oxide
Polymer Sensors

## Slide 32: Polymer Sensors
Autocalibration for Low-Level Stability
Composite Sensor Structure

## Slide 33: Polymer Sensor Versatility
Fast Response Time
Recovery from water spikes or condensation
Exposure to compressor oils
Special Conditions
Portable Sampling Systems
Wide Measurement Ranges
Key Performance Issues
Custom Variations

## Slide 34: Sensor Response Times
Thin film Polymer sensor has a response time 20 times faster compared to Aluminum Oxide sensors (Frost point change from -76 °C to -40 °C)
Polymer sensor
Polymer sensor
Ceramic sensor
Ceramic sensor

## Slide 35: Selecting the Right Instrument - Conditions
What is the expected dewpoint level at the measurement location?
What is the pressure range?
What is the temperature range?
ISO 8573.1 Standard

## Slide 36: Selecting the Right Instrument - Installation
Will the probe be installed directly in the line or will a sample line be used for external measurement?
Should the instrument be portable or fixed mount?

## Slide 37: Selecting the Right Instrument - Communication
Signal output type– local display, analog, serial, IoT
Other features of interest – power supply, datalogging, alarm relays

## Slide 38: Calibration & Maintenance
Leak Detection
Calibration
Point Of Use Quality Control
Highest Possible Accuracy
Spot Checking
Factory Calibration

## Slide 39: Field Calibration Resources
Portable
Direct Connection
Interfacing
Portable Instruments
Software Solutions

## Slide 40: …it’s more important than ever to base decisions on accurate and reliable data.
Thank You

## Slide 41
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Measuring Dew Point for Process Safety, Quality and Efficiency
Sponsored by

## Slide 42: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within 2 days.

## Slide 43
Thursday, November 12, 2020 – 2:00 PM EST
Register for free at
www.airbestpractices.com/magazine/webinars
November Webinar Measuring KPI’s: kW, Flow, Pressure, Dew Point
Sponsored by
Tim Dugan
Keynote Speaker
Compression Engineering Corporation