## Slide 1
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to attendees within two days.
Visualizing KPI’s: Specific Power, Flow, Pressure, Dewpoint
Ron Marshall, Marshall Compressed Air Consulting
Keynote Speaker
Sponsored by

## Slide 2: Q&A Format
Panelists will answer your questions during the Q&A session at the end of the Webinar.
Please post your questions in the Questions Window in your GoToWebinar interface.
Direct all questions to Compressed Air Best Practices® Magazine
Sponsored by

## Slide 3: Handouts

## Slide 4: Disclaimer
All rights are reserved. The contents of this publication may not be reproduced in whole or in part without consent of Smith Onandia Communications LLC. Smith Onandia Communications LLC does not assume and hereby disclaims any liability to any person for any loss or damage caused by errors or omissions in the material contained herein, regardless of whether such errors result from negligence, accident, or any other cause whatsoever.
All materials presented are educational. Each system is unique and must be evaluated on its own merits.

## Slide 5
Introduction by Rod Smith, Publisher
Compressed Air Best Practices® Magazine
Visualizing KPI’s: Specific Power, Flow, Pressure, Dewpoint
Sponsored by

## Slide 6: 2019 Best Practices EXPO & Conference

## Slide 7: 2019 Best Practices EXPO & Conference
The conference will focus on the industrial plant utilities of compressed air, blower, vacuum and cooling systems. Presentations should encompass one or more of these themes.
Call for Abstracts
Quality & Safety Management
Maintaining compliance
Facility Maintenance & Reliability
Maintaining systems
Productivity / Energy Intensity
Increasing product output
Energy Management / Water Intensity
Reducing product rejects and liabilities
Increasing equipment longevity
Reducing kw per product produced
Reducing water usage across utilities
Energy monitoring and IoT
Creating an energy management culture
  Abstract submissions are due Friday, March 29, 2019.
  Speakers receive a complimentary Conference Pass, a $675 value!
  To submit an abstract, please visit
  cabpexpo.com/conference/speakers

## Slide 8: About the Speaker
Chief Auditor, Marshall Compressed Air Consulting
38 year Employee of Power Utility
24 years Technical Compressed Air Support
Compressed Air Challenge Level 2 Instructor
International Trainer for United Nations Industrial Development Organization (UNIDO)
Sponsored by
Ron Marshall
Marshall Compressed Air Consulting

## Slide 9: Visualizing KPI’s: Specific Power, Flow, Pressure, Dewpoint

## Slide 10: Presenter

## Slide 11: Coming Up
What are Key Performance Indicators?
Why KPI’s are important in compressed air?
Typical Compressed Air System
Suggested KPI’s or EnPI’s
Suggested Measurement Points
Analysis: What to look for in meeting objectives
Typical Problems in Measuring and Tracking
Examples of Best Practices

## Slide 12: What are Key Performance Indicators?
A performance indicator or key performance indicator (KPI) is a type of performance measurement. KPI’s evaluate the success of a particular activity.
Source: Wikipedia

## Slide 13: What are Key Performance Indicators?
Often success is simply the repeated, periodic achievement of some levels of operational goal
Sometimes success is defined in terms of making progress toward strategic goals.
Accordingly, choosing the right KPI’s relies upon a good understanding of what is important.
What is deemed important often depends on the department measuring the performance.
Source: Wikipedia

## Slide 14: What are Key Performance Indicators?
KPI assessments often lead to the identification of potential improvements, so performance indicators are routinely associated with 'performance improvement' initiatives.
Source: Wikipedia

## Slide 15: What Makes KPI’s effective?
A key performance indicator it is only as valuable as the action it inspires.
One of the most important, but often overlooked, aspects of KPIs is that they are a form of communication. As such, they abide by the same rules and best-practices as any other form of communication. Succinct, clear and relevant information is much more likely to be absorbed and acted upon.
Source: Klipfolio.com

## Slide 16: Why KPI’s are important in compressed air?
Compressed air is a very expensive way to transmit energy, typically 10 times more costly than direct electricity
There are usually very few performance measurements done on compressed air
Unmanaged systems often produce compressed air very inefficiently, operators are usually unaware
Unmanaged system typically have high levels of waste, operators are often aware but don’t know the cost
Measuring the key performance of a system raise awareness of the cost of inefficiency and waste
A good system of measuring and evaluating KPI’s can lead to substantial improvements in cost of operation, reliability and quality of compressed air

## Slide 17: Compressed Air: What is most important?
Clean dry stable air being delivered at the appropriate pressure in a cost effective manner
Minimized waste
  Leaks
  Artificial Demand
  Inappropriate Use
How do we know we are getting this?
Measuring performance is key
Measurements are compared to benchmark to determine success in meeting goals
Source: Compressed Air Challenge

## Slide 18: Example Spot Measurement
Pressure Key Performance
Source: Compressed Air Challenge
Key Performance Fail
Key Performance Success

## Slide 19: Example Time Based Measurement
Site Goal: Pressure no lower than 90 at critical tools
Site appears to meet goals

## Slide 20: Example Time Based Measurement
Site Goal: Pressure no lower than 90 at critical tools
Correctly placed metering shows key performance fail 87 psi
Spot reading
Low pressure event

## Slide 21: Example Time Based Measurement
Site Goal: Minimize waste, run compressors efficiently
Flow metering shows KPI fail during non-production times
Compressor input 135 kW at 500 cfm = 27 kW/100 cfm
KPI fail since target is 20 kW/100 cfm, leaks < 200
Waste
Low flow

## Slide 22: Example Time Based Measurement
Site Goal: Minimize waste, run compressors efficiently
Flow metering shows step change in non-production flow
Compressor input 108 kW at 325 cfm = 28.5 kW/100 cfm
325 cfm
500 cfm

## Slide 23: Measuring KPI’s Important Points
Spot checks don’t show the whole picture
Meter placement must match site goals
Things can change as time passes, limits or method of comparison needed
KPI levels need to be set
Needs to be a communication system to alert of failure

## Slide 24: Guidance on KPI’s: CSA C837-16 Standard
Measurement Boundary
Measure all inputs (kW)
Measure all outputs (cfm)
Track relevant variables (pressure, hours, units production)
Source: CSA C837-16

## Slide 25: Guidance on KPI’s: CSA C837-16 Standard
Suggested KPI’s or Energy Performance Indicators (EnPI’s)
System Specific Power (SSP)
Total Energy Consumption (TEC)
Specific Energy Consumption (SEC)
Proportion of Non-productive Usage (PNPU)
Source: CSA C837-16

## Slide 26: Guidance on KPI’s: CSA C837-16 Standard
SSP (kW/100 cfm or kWh/m3)
Average kW sent into the measurement boundary divided by average flow coming out x 100, during the measurement period.
An output of this might be average kW per 100 cfm.
This is an indicator of how efficiently the compressed air is being produced.
SSP changes with discharge pressure, so pressure should be tracked
Source: CSA C837-16

## Slide 27: Guidance on KPI’s: CSA C837-16 Standard
TEC (kWh)
TEC is a measure of the total energy (kWh) consumed by a over the baseline period. The lower the energy consumed, the lower the electrical cost of operation.
Provided that the TEC can be normalized for time period and production levels, two different TEC measurements of the same system taken at different times may be used for comparative evaluation.
TEC is affected by both the SSP of the compressed air production equipment and the total volume of compressed air produced by the system during the baseline period.
Based on site electrical rates the operating costs can be determined
Source: CSA C837-16

## Slide 28: Guidance on KPI’s: CSA C837-16 Standard
Optional: SEC (kWh per unit of product)
SEC is a measurement of the compressed air system energy required to produce a specified production output
Subject to an accurate characterization of the specified production output, the lower the SEC, the lower the energy intensity of the compressed air per specified production unit
The output of the product unit is subject to a great deal of variability depending on the characteristics of the facility and any production processes. This value may or may not be a useful output and the requirement for its calculation needs to be determined on a case by case basis.
Source: CSA C837-16

## Slide 29: Guidance on KPI’s: CSA C837-16 Standard
PNPU (percentage of average flow)
PNPU is an estimate of the percentage non-productive air consumption compared to the average flow.
The value is the air flow measured or calculated, during special testing, divided by the average air flow during the same baseline period
In all systems there is some compressed air flow consumed by equipment and processes due to leakage, and air consuming equipment that is operating in non-production hours.
In systems where there is a period of time where there is no production during shutdown periods, such as evenings or weekends, this flow may be measured or estimated.
Source: CSA C837-16

## Slide 30: Use of KPI’s
Determine when KPI’s are above or below expected target levels
Compare one measurement period to another (after improvements, failures)
Source: CSA C837-16

## Slide 31: Additional KPI’s
Additional Parameters (user can decide)
Air pressure (high/low/average)
Temperatures (compressor, dryer, ambient)
Dew point
Contamination levels (particles, lubricant, dew point)
Other parameters as can be measured (downtime, availability)

## Slide 32: Example Systems
Most common parameters pressure, amps/power and flow
More sophisticated systems show system efficiency
Some include other items like air dryers
Determination of non-productive flow is important but not always possible
Placement of the meters sometimes affects readings
Processing of the data is sometimes needed (moving averages)
Certain conditions can cause erroneous readings

## Slide 33: Example Systems
Simple monitoring system – needs high level of interpretation
Confusing and unclear data, manual KPI calculation required
Measurement error due to flow meter position

## Slide 34: Example Systems
Simple monitoring system – needs high level of interpretation
Moving average applied makes data clearer
Flow meter error when compressor is off must be subtracted out

## Slide 35: Example Systems – Web Based
Source: CALMS.EU

## Slide 36: Example Systems – Web Based
Source: CALMS.EU

## Slide 37: Example Systems – Web Based
Source: CALMS.EU

## Slide 38: Example Systems – Web Based
Source: Sparksdynamics.com

## Slide 39: Example Systems – Web Based
Source: Sparksdynamics.com
See Jan/Feb 2019 CABP

## Slide 40: Example Systems – Web Based
Source: Sparksdynamics.com

## Slide 41: Example Systems – Web Based
Source: Lightapp.com as featured in Aug 2018 CABP

## Slide 42: Example Systems – Web Based
Source: Lightapp.com as featured in Aug 2018 CABP

## Slide 43: Example Systems – Web Based
Source: Kaeser
Source: EnergAir.com

## Slide 44: Example Systems – Web Based
Source: Kaeser
Source: EnergAir.com

## Slide 45: Example Systems – Controller Based
Source: Kaeser

## Slide 46: Example Systems – BMS based
User Designed System

## Slide 47: Example Systems – Controller Based
Source: VPInstruments

## Slide 48: Important Points
Compressed air systems should be measured
Output of monitoring system needs to be clear and simple
Best practice is to monitor and track both production efficiency and waste
Communication and interpretation of problems must be easy to understand
Email notification of KPI’s daily, weekly or monthly is a good way of continuously monitoring systems

## Slide 49: Recommended Measurements
Capture the full measurement boundary
Display on simple dashboard
Pressure
  Discharge
  Dryer
  Critical Uses
Power
  Compressor
  Dryers
Flow
  Main
  Submetering
Important KPI’s
Dew Point
Temperatures
Warnings/Alarms

## Slide 50: Summary
KPI’s are important to maintain system efficiency and effectiveness, reduce costs
It is important to capture all data and relevant variables
Monitoring systems can be used to identify problems and track changes
Sometimes there are challenges in correctly monitoring
Some processing of the data may be required
The best systems display data in an a way that is effective and easy to understand, and alert the operators if there are problems
There are various systems available to calculate and monitor KPI’s

## Slide 51: About the Speaker
Sales Manager Americas, VPInstruments
Menno Verbeek
VPInstruments

## Slide 52
30%
LEAKS
300$
Costs
10
Efficiency
1.5h
Down time
Visualizing KPI’s
Specific Power, Flow, Pressure, Dewpoint
1
Notes: Key Performance Indicator
Indicators that tell you if processes and machinery are okay, if consumption and usage is within acceptable boundaries, if metrics start to deviate to help spot early problems, if the input ratio matches the output ratio.

## Slide 53
2
Notes: Not looking at the right data, your performance indicators and instrumentation might leave you stranded..

## Slide 54: Why KPI’s are important
        Know where you are
        and where you’re going…
        Company purpose
        Savings goal
        Production goal
        Maintenance goal
        Compliance goal
3

## Slide 55: Why KPI’s are important
        SMART KPI’s
        Simple
        Monitored permanently
        Accounted for
        Realistic
        Trendable
4
Notes: Nieuwe definitie van SMART ;-)

## Slide 56: Compressed air KPI’s
Supply side
Energy costs per compressor room
Specific power/Efficiency per 100*SCF or kW/m3n/min
Quality (dew point)
Purity (N2)
Demand side
Leakage % and $$$ per annum
Return on Repairs
Pressure loss
Costs per widget/tons produced
Production (repair/incident) downtime per machine
5
Notes: Express leakage always in USD per dept.
Leakage is the messenger for more trouble to come, early warning for possible longer down time
Cost for repair vs return

## Slide 57: Keep it Simple: start with 3 KPI’s
Maintenance:
      Leakage %
      Dew point & flow
      Running hours vs downtime hours
      Number of CA related incidents
Finance:
      costs per…
      MSCF of air
      Cost per x ton products
Production:
      Pressure band
      Cost per x ton products
      Allocate costs/ consumption per area
6
Notes: When you’re new with KPI’s, then keep it simple. Too difficult KPI’s result in less buy in, lack of attention and have no priority over time.

## Slide 58: How permanent monitoring can help
Data is your starting point
Combine data!
Key data
Amps or Kw
Flow
Pressure
Temperature
Dew point
X products
10
Efficiency
2
DP/Demand
8
Cool reserve
9
Dryer capacity
6
kW/x Ton
7
Notes: Amps/kw + Flow = efficiency
Flow + pressure = dif. pressure = pressure loss
Flow + temp = water cooling may become questionable during summer season
Flow + dewpoint = dryer capacity or dryer failure
Amount of kW per amount of product produced

## Slide 59: Real time KPI example: efficiency
A/B
Flow meter
kW meter
> 12?
> 10 < 12?
< 10?
8
Notes: Make scaling on good, bad performance with compressor curve or comp. performance data.
Thing become more complicated with multiple compressors, it then may require a specialist or specialized software

## Slide 60: How you could make it visual
9

## Slide 61: Efficiency for multiple compressors not so easy…
10
Notes: Warning: efficiency monitoring is probably one of the most complex tasks. Many factors can influence the system efficiency…

## Slide 62: Efficiency for multiple compressors not so easy…
11

## Slide 63
50
Leakage %
Common issues:
Leaking membrane valves
Don’t know which one leaks
Hard to access, no time to inspect all
Solution:
Permanent flow meter on main supply
Flow meter on each filter system
Central monitoring via VPVision
Added value
Real time leakage management
Optimized maintenance schedules
ROI: ½ year
12
Notes: An example of how monitoring and metering helped lowering costs and improve operational uptime.
Flow meter became permanent part of KPI for flow. When flow increased membranes were likely to leak/be broken

## Slide 64: Audit vs permanent
Long term data is key
Chart: Energy consumption
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
No audit | 10 | 12 | 17 | 18 | 22 | 24 | 26 | 30 | 34 | 44 | 52 | 65
Periodical audit | 10 | 12 | 17 | 18 | 22 | 10 | 12 | 17 | 18 | 22 | 24 | 26
Permanent monitoring | 10 | 12 | 13 | 11 | 13 | 12 | 10 | 11 | 12 | 13 | 12 | 11
13
Notes: The case before would never have led to the saving without permanent monitoring. An audit might have revealed some, but after the fix, you would not know where it leaks next.
It is all about collecting data. Collecting just flow is useless, just as collecting just energy or just pressure. It is in the combination of data where you find the biggest saving opportunities.

## Slide 65: Real time KPI: Air treatment pressure loss
DP monitoring without flow sensor? Makes no sense at all.
(P1-P2)/Q
Flow [Q]
Pressure 1
Pressure 2
> factor?
Filter
Filter
Filter
P1
P2
Q
-
14
Notes: You can have low flow and almost no pressure drop over the filter.
When recording pressure drop over your filter you want to know at which flow.
Did we reach max capacity of the filter of is it clogged?

## Slide 66: Real time KPI: Air treatment pressure loss
Chart: DP vs flow
| 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 120
NEW FILTER | 0 | 0.063913 | 0.25565 | 0.57522 | 1.0226 | 1.5978 | 2.3009 | 3.1318 | 9.2035
OLD FILTER | 0 | 0.12783 | 0.51131 | 1.1504 | 2.0452 | 3.1957 | 4.6018 | 6.2635 | 12.7827
DP monitoring without flow sensor? Makes no sense at all.
30
210
180
150
120
90
60
NORMAL 100% FLOW DP LEVEL
FILTER POTENTIAL BURST LEVEL
15

## Slide 67: Dew point measurement
Just measuring dew point is not enough.
You want to be looking at dew point and flow.
16
Notes: Hey! Dew point went up! You might run out to the dryer, inspect it and find it being okay. Without flow this graph is nice but not giving the complete picture.

## Slide 68: Real time KPI: Drying capacity
See when demand exceeds capacity
17
Notes: When dew point is critical, always measure after dryer and storage tank and in the main line feeding the plant. Dryers can be bypassed during service, storage can have non working drains, and just taking dew point of the dryer is not a guarantee that this same dew point level is maintained in the plant.

## Slide 69: Real time KPI: Drying capacity
18
Notes: And because we are here at Air best practices, when dew point is critical, dryers should always be in parallel with the compressor and each compressor should have its dedicated dryer.

## Slide 70: Flow and dew point
Chart: Flow and dew point go up
Chart: Flow is stable, dew point goes up
19
Notes: Picture 1: capacity related
Picture 2: dryer related. Cycle related, drain related, etc.

## Slide 71: Monitoring example dashboard
20

## Slide 72: Where to start?
Efficiency monitoring
Air quality and flow
Cost allocation /
demand profile
21
Notes: Efficiency: depending on how accurate you want it, an Amp meter of 3 phase power meter with a flowmeter suitable for saturated air measurement. Either per compressor or per compressor room.
Dewpoint and flow, they always should go together
Flow sensors with flow and pressure to continuously measure flow consumption and pressure. When calculation your dollar/scf allocating cost becomes a piece of cake

## Slide 73: Where to start?
Allocate cost /usage per shift
Measure pressure
loss throughout
the plant
Cost per X
22
Notes: Simple measure on subline to dedicated machines / operators tell mass flow used by shift/operator/machine
By adding pulse counter cost per X can be calculated
Pressure throughout the plant: pressure band monitoring

## Slide 74: Example Report
23

## Slide 75: KPI example Report
24

## Slide 76: Summary
Define your top 3
Collect your primary data (energy, flow, pressure, dew point, products produced)
Combine data to create better information
Report the data
Share data on an accessible dashboard for all
Make system changes based on facts!
25

## Slide 77
26

## Slide 78
27

## Slide 79
Please submit any questions through the Question Window on your GoToWebinar interface, directing them to Compressed Air Best Practices Magazine. Our panelists will do their best to address your questions, and will follow up with you on anything that goes unanswered during this session.
Thank you for attending!
Q&A
Visualizing KPI’s: Specific Power, Flow, Pressure, Dewpoint
Sponsored by

## Slide 80: Thank you for attending!
The recording and slides of this webinar will be made available to attendees via email later today.
PDH Certificates will be e-mailed to Attendees within two days.
Sponsored by

## Slide 81: 2019 Best Practices EXPO & Conference

## Slide 82: 2019 Best Practices EXPO & Conference
The conference will focus on the industrial plant utilities of compressed air, blower, vacuum and cooling systems. Presentations should encompass one or more of these themes.
Call for Abstracts
Quality & Safety Management
Maintaining compliance
Facility Maintenance & Reliability
Maintaining systems
Productivity / Energy Intensity
Increasing product output
Energy Management / Water Intensity
Reducing product rejects and liabilities
Increasing equipment longevity
Reducing kw per product produced
Reducing water usage across utilities
Energy monitoring and IoT
Creating an energy management culture
  Abstract submissions are due Friday, March 29, 2019.
  Speakers receive a complimentary Conference Pass, a $675 value!
  To submit an abstract, please visit
  cabpexpo.com/conference/speakers

## Slide 83
Thursday, March 14, 2019 – 2:00 PM EST
Register for free at
www.blowervacuumbestpractices.com/magazine/webinars
Tim Dugan
Compression Engineering Corporation
Keynote Speaker
March 2019 Webinar How to Design a Centralized Vacuum System
Sponsored by